## Slide 1: Reservoir Modeling Methodologies
Advanced Applications of HEC-HMS
June 2024
Jay H. Pak, Ph.D., P.E.
Sr. Research Hydraulic Engineer
US Army Corps of Engineers
Hydrologic Engineering Center

## Slide 2: Purpose
Understand and apply appropriate reservoir modeling techniques in HEC-HMS

## Slide 3: Outline
Reservoir element overview
Specified release
Outflow curves
Outflow structures
Rule-based routing
Reservoir Sediment Routing

## Slide 4: Reservoir Element Overview

## Slide 5: Reservoir Routing
A hydrological process used to predict the temporal changes in water storage, inflow, and outflow of a reservoir. This process relies on elevation-area and elevation-storage curves to understand the relationship between the water level (elevation) and both the surface area and volume of the reservoir.

## Slide 6: Reservoir Element
One of the seven basin model element types
One upstream element
Up to two downstream elements
  Main
  Auxiliary
Five routing methods
  None, Outflow Curve, Outflow Structures, Rule-Based Operations, Specified Release

## Slide 7: Geometry (Storage Method)
Reservoir computes the continuity equation
Outflow Curve | Outflow Structures | Rule-Based Operations | Specified Release
Elevation-Area-Discharge | Elevation-Area | Elevation-Area | Elevation-Area
Elevation-Storage-Area-Discharge | Elevation-Storage | Elevation-Storage | Elevation-Storage
Elevation-Storage-Discharge | Elevation-Storage-Area | Elevation-Storage-Area | 
Storage-Discharge (Simplest Option) |  |  | 
Sediment Routing Available Method

## Slide 8: Initial Conditions
State information required for simulation start
Available options depend on selected storage method
  Storage (simplest)
  Elevation
  Discharge
  Inflow = Outflow
Notes: The Discharge method is available for outflow curves – since storage and outflow are 1:1 related, the initial storage can be determined
The Inflow = Outflow method takes the inflow to the reservoir at the beginning of the simulation and determines the pool elevation necessary to cause that outflow through the outlet structures. The pool elevation is then used in the elevation-storage curve to determine the matching storage.

## Slide 9: Simulation Results
Notes: The top plot is for geometry – it shows the reservoir’s storage and elevation for the simulation. Not all routing methods will have an elevation plot, but all of them must compute storage.
The bottom is for flow – the reservoir inflow is dashed, and outflow is solid.

## Slide 10: Reservoir Options Tab
Notes: Observed outflow allows you to set a discharge gage as an observed flow series that you can compare your results to
Observed tailwater stage lets you set a stage gage as an observed stage time series that you can compare computed tailwater stages to (requires a tailwater rating curve)
Observed pool elevation is pretty self-explanatory
Tailwater stage-discharge lets you set a rating curve for the tailwater – this can be important for computing hydraulic structure submergence.
The reference flow and label are for making a nice label on your simulation results graph.

## Slide 11: Best Practices
Use a junction upstream and downstream of your reservoir
Calibrate/validate your model isolating out the reservoir first
  Use Specified Release method to pass the right flows downstream
Keep it simple
  HMS is not ResSim

## Slide 12: “None” Routing Method
“--None--” will pass flow downstream with no routing

## Slide 13: Specified Release

## Slide 14: Specified Release
Used when the outflow from a reservoir is known
Elevation/storage computed from simulated inflow and specified outflows

## Slide 15: Specified Release
Outflow specified as a discharge gage
Optional settings: Max Release, Max Capacity
  Settings do not alter outflows, only produce warnings

## Slide 16: Specified Release – When to Use?
Calibration/validation phase of model construction
Releases are determined by something external to HMS

## Slide 17: Outflow Curves

## Slide 18: Outflow Curves
Reservoir outflow is determined solely by storage
Ideal for reservoirs with no gates/operations
Can be “calibrated” to represent more complex reservoirs
Notes: This gets quite a bit of use for detention basin design – most have simple geometry and outflow relationships that makes modeling them very easy.

## Slide 19: Outflow Curves – Storage Method
Simplest option is the Storage-Discharge storage method
Other methods will compute elevation
Notes: The “Primary” setting just determines the interpolation scheme. The Outflow Curve method builds a big table for all the geometry variables involved, and the one set as “primary” determines the initial configuration of the table (what rows the other tables are interpolated to.)

## Slide 20: Outflow Curve Calibration
Works best when operations are simple
Iterative process
  Build curve
  Run simulation
  Check stage/storage/ outflow
  Modify curve

## Slide 21: Outflow Curves – When to Use?
Outflow is always the same for a given storage
  Ungated outlets/spillways, dam tops, etc.
Operations can be reasonably simplified to a single curve
Long Term Reservoir Volume Reduction Analysis

## Slide 22: Outflow Structures

## Slide 23: Outflow Structures
Outflow computed by a collection of hydraulic structures
  Outlets
  Spillways
  Dam tops
  Pumps
Simulate other kinds of outflows
  Dam breaks
  Dam seepage
  Time-series releases
  Monthly Evaporation

## Slide 24: Outlets
Orifice Outlet
Culvert Outlet
Always submerged
Can flow partially full
https://www.hec.usace.army.mil/confluence/hmsdocs/hmstrm/modeling-reservoirs/outlets

## Slide 25: Spillways
Broad-Crested
Ogee
Specified
https://www.hec.usace.army.mil/confluence/hmsdocs/hmstrm/modeling-reservoirs/spillways

## Slide 26: Spillway Gates
Sluice Gate
Radial Gate
https://www.hec.usace.army.mil/confluence/hmsdocs/hmstrm/modeling-reservoirs/spillways
Notes: Note that the only control method is “Fixed Opening” – the gates do not move during the simulation. This will compute the hydraulics through a gate at a fixed setting.

## Slide 27: Dam Tops
Level
Non-Level
https://www.hec.usace.army.mil/confluence/hmsdocs/hmstrm/modeling-reservoirs/dam-tops

## Slide 28: Pumps
https://www.hec.usace.army.mil/confluence/hmsdocs/hmstrm/modeling-reservoirs/pumps

## Slide 29: Tailwater
Controls determination of submergence for structures
5 options:
  Assume None
  Reservoir Main Discharge (requires rating curve)
    Computed at outlet – no backwater
  Downstream of Main Discharge (requires rating curve, E-D)
    Computed (Elevation) at next element downstream
  Specified Stage (requires stage time series)
  Fixed Stage

## Slide 30: Outflow Structures – When to Use?
Complex combination of ungated hydraulic structures
Need to compute dam breaks, seepage, or evaporation

## Slide 31: Rule-Based Reservoir Routing

## Slide 32: Guide Curve Operations
Above the Guide Curve
  increase releases as necessary (or possible) to lower the pool elevation to the Guide Curve.
Below the Guide Curve
  reduce releases as necessary (or possible) to raise the pool elevation to the Guide Curve.
At the Guide Curve
  release “just enough” to maintain the pool elevation at the Guide Curve
Notes: There are three states in guide curve ops.
You can be right on the guide curve (see the yellow dot.) For the day of the year, the reservoir has the desired storage.
You can be above the guide curve (see the blue dot.) For the day of the year, the reservoir is storing more than desired.
You can be below the guide curve (see the orange dot.) For the day of the year, the reservoir is storing less than desired.

## Slide 33: Rule-Based Reservoir Routing
Extension of Outflow Structures routing method
Uses rules and operable structures to determine releases
Zones determine what rules are applied
  Reservoir elevation
  Day of the year

## Slide 34: Zones
A grouping of homogeneous rules
Defined by an elevation range and day of year for each zone
  Finds first Maximum Elevation curve above the current elevation/day
Need at least one for operations to work

## Slide 35: Maximum Elevation
Each Zone is defined by a maximum elevation, which is a Daily Elevation Pattern Paired Data curve.

## Slide 36: Maximum Elevation
Daily Elevation Pattern Paired Data
Top zone should cover entire range of elevations and dates
Curve does not need to be defined for every day of the year
  If nothing defined, zone will not be used for that day
Schedule A Non-Growing Season
Schedule A Growing Season
Notes: In the example on the right, a regulation manual calls its basic flood operations “Schedule A”. The dam has the potential to cause agricultural damages, so maximum releases are limited during the growing season compared to the non-growing season, so despite these having the same overall elevation (707 ft) the rules they contain would be different.

## Slide 37: Storage Objective (Guide Curve)
For every day of the year, what is the desired storage?
Currently able to be defined for each zone
  May change to a single guide curve for the Dam in the future
  Recommend using only one for all zones unless you have really specific needs
Interpolates between points
Needs to cover entire year
Flood Pool
Conservation Pool

## Slide 38: Rules
Added via Zone
Rules are specific to a single zone

## Slide 39: Rule Types (10)
Type | Limits | Operation
Main Release | Min, Max, Specified | Sets a target for releases in the main direction
Auxiliary Release | Min, Max, Specified | Sets a target for releases in the auxiliary direction
Downstream Flow* | Min, Max, Specified | Sets a target for an element downstream
Rate of Flow Change | Max | Limits how much releases can change per each time
*requires iterative trial releases

## Slide 40: Rules
No limit to what you can specify
Try not to make them conflict

## Slide 41: Downstream Controls
Require iterative trial releases
Significantly add to simulation time
Keep them as simple as possible

## Slide 42: Outflow Structures
All features of Outflow Structures method available
Only some structures have parts that can be operated
  Outlets
    General Outlet
    Gated Orifice
  Broad-Crested and Ogee Spillways
    Radial Gates
    Sluice Gates

## Slide 43: General Outlet
Gate Control Methods

## Slide 44: Gated Orifice Outlet

## Slide 45: Gated Spillway
Operable sluice and radial gates for Broad-Crested and Ogee spillways

## Slide 46: Calibration
Isolate reservoir by using a source element with a timeseries gage
Calibration by adjusting rules
  These may deviate from the regulation manual
  Add other rules or settings for stability
    Rate of change rules help even if not included in WCM
Calibration by adjusting structures
  Adjust rating curves for outlets or spillways using simple methods

## Slide 47: Rule-Based Reservoir Routing – When to Use?
Storage target and releases vary seasonally
Complex rules and operable structures determine releases
You might be surprised how effective simple guide curve operations can be for many models!

## Slide 48: Reservoir Sediment Routing

## Slide 49: RESERVOIR sediment ROUTING PROCESSES
Reservoir
Reservoir Outlet
Watershed Outlet/Channel Outlet
Brune Sediment Trap
100% Sediment Trap
Volume Ratio
Dynamic Reservoir Volume Reduction (Updating E-A & E-S curves)
Fall Velocities:
Rubey
Van Rijn
Toffaleti
Report 12
Richardson and Zaki (1954)
Kumbhakar (2017)
Channel
0% Sediment Trap
Specified Sediment Trap
Chen Sediment Trap
2-Deposition Shape Option for Each Grain Size (V-Shape or Elongated Taper)

## Slide 50: Reservoir Volume Reduction Process
Clay, Slit, Sand & Gravel: 2-Optopn (V-Shape or Elongated Taper)

## Slide 51: Chen’s Sediment Trap (Chen 1975)
Critical settling velocity
Trapping Efficiency
    Stratified (quiescent) reservoir (upper bound)
    Mixed (turbulent) reservoir (lower bound): Chen, 1975
      The settling velocity is computed using the method selected for the Basin Model.
      The critical settling velocity is computed as the discharge rate (Q) from the reservoir divided by the surface area (A). The computations are performed separately for each grain size class or subclass.
Source: Verstraeten, G and Poesen, J., Estimating trap efficiency of small reservoirs and ponds: methods and implications for the assessment of sediment yield, Progress in Physical Geography 24, 2 (2000), pp. 219-251.

## Slide 52: Brune’s Sediment Trap (Brune 1953)
Capacity/Annual Inflow Ratio
      Vres = Reservoir Capacity
      Vinflow = Annual Inflow (A user specified initial value is required)
Trapping Efficiency
      a = Coefficient (Low=95, Medium=97, High=100)
      b = Coefficient (Low=5.37, 6.42, High=7.71)

## Slide 53: Methodology
Sediment deposition
Suspended sediment
Outflow sediment

## Slide 54: Reservoir volume reduction calculation process
Bottom Layer
Sediment Inflow
Clay = 200 T/d
Silt = 70 T/d
Sand = 1 T/d
Trap Efficiency (TE)
Clay = 0.7
Silt = 1
Sand = 1
Sediment Deposit=Sediment Inflow X TE
Silt = 140 T/d
Sand = 70 T/d
Gravel = 1 T/d
X
Suspended Sediment =
Sediment Inflow-Sediment Deposit
Clay = 60 T/d
Silt = 0 T/d
Sand = 0 T/d
Sediment Outflow
Clay = 60 T/d
By
Volume Ratio

## Slide 55: HEC-HMS GUI for two sediment trap efficiency Methods

## Slide 56: Tuttle Creek Results with Reservoir Volume Reduction
Chart: Elevation (ft, NVGD29)
MPP Elevation | 0 | 300000

## Slide 57: Questions?